{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":68,"n_cols":10,"rows_kept":68,"merged":[[0,0,31,0],[32,0,67,0],[41,7,51,7]],"flags":["formulas_cached_only"]}
["数采板1","A0","375V接地模拟量1","PE3","ADC0"]
[null,"A1","375V接地模拟量2","PE2","ADC1"]
[null,"A2","48V接地模拟量1","PE1","ADC2"]
[null,"A3","48V接地模拟量2","PE0","ADC3"]
[null,"A4","24V接地模拟量1","PK0","ADC16"]
[null,"A5","24V接地模拟量2","PK1","ADC17"]
[null,"A6","12V接地模拟量1","PK2","ADC18"]
[null,"A7","12V接地模拟量2","PK3","ADC19"]
[null,"A8","375V电压监测","PB5","ADC11"]
[null,"A9","375V电流监测","PB4","ADC10"]
[null,"A10","48V电压采样","PE4","ADC9"]
[null,"A11","48V电流采样","PE5","ADC8"]
[null,"A12","影像电压采样","PD4","ADC7"]
[null,"A13","影像电流采样","PD5","ADC6"]
[null,"A14","12V电压采样","PD6","ADC5"]
[null,"A15","12V电流采样","PD7","ADC4"]
[null,"Din1","通道1故障","PM7"]
[null,"Din2","通道2故障","PM6"]
[null,"Din3","通道3故障","PM5"]
[null,"Din4","通道4故障","PM4"]
[null,"Din5","通道5故障","PB2"]
[null,"Din6","通道6故障","PB3"]
[null,"Dout1","375V接地检测控制2","PN4"]
[null,"Dout2","375V接地检测控制1","PN3"]
[null,"Dout3","48V接地检测控制2","PN2"]
[null,"Dout4","48V接地检测控制1","PN1"]
[null,"Dout5","24V接地检测控制2","PN0"]
[null,"Dout6","24V接地检测控制1","PP5"]
[null,"Dout7","12V接地检测控制2","PP4"]
[null,"Dout8","12V接地检测控制1","PP3"]
[null,"Dout9","接地检测板控制口","PL4",null,"高电平工作"]
[null,"串口3","数采板2串口3"]
["数采板2","A0","24V电压监测","PE3","ADC0"]
[null,"A1","24V电流监测","PE2","ADC1"]
[null,"A2","漏水模拟量1","PE1","ADC2"]
[null,"A3","漏水模拟量2","PE0","ADC3"]
[null,"A4","通道1电流采样","PK0","ADC16"]
[null,"A5","通道2电流采样","PK1","ADC17"]
[null,"A6","通道3电流采样","PK2","ADC18"]
[null,"A7","通道4电流采样","PK3","ADC19"]
[null,"A8","通道5电流采样","PB5","ADC11"]
[null,"A9","通道6电流采样","PB4","ADC10",null,null,"注：","CO2","通道1"]
[null,"A10","通道7电流采样","PE4","ADC9",{"$nulls":3},"CTD","通道2"]
[null,"A11","通道8电流采样","PE5","ADC8",{"$nulls":3},"UV1","通道3"]
[null,"A12","通道9电流采样","PD4","ADC7",{"$nulls":3},"UV2","通道4"]
[null,"A13","通道10电流采样","PD5","ADC6",{"$nulls":3},"UV3","通道5"]
[null,"A14","通道11电流采样","PD6","ADC5",{"$nulls":3},"UV4","通道6"]
[null,"Din1","通道7故障","PM7",{"$nulls":4},"多参数","通道7"]
[null,"Din2","通道8故障","PM6",{"$nulls":4},"ADCP","通道8"]
[null,"Din3","通道9故障","PM5",{"$nulls":4},"12V备","通道9"]
[null,"Din4","通道10故障","PM4",{"$nulls":4},"24V备","通道10"]
[null,"Din5","通道11故障","PB2",{"$nulls":4},"48V备","通道11"]
[null,"Dout1","通道1控制","PN4"]
[null,"Dout2","通道2控制","PN3"]
[null,"Dout3","通道3控制","PN2"]
[null,"Dout4","通道4控制","PN1"]
[null,"Dout5","通道5控制","PN0"]
[null,"Dout6","通道6控制","PP5"]
[null,"Dout9","通道7控制","PL4"]
[null,"Dout10","通道8控制","PL3"]
[null,"Dout11","通道9控制","PL2"]
[null,"Dout12","通道10控制","PL1"]
[null,"Dout13","通道11控制","PM0"]
[null,"Dout14","通道12控制","PM1"]
[null,"串口2","温湿度（485）"]
[null,"串口4","惯导（TTL）"]
[null,"串口6","串口服务器"]
[null,"串口3","数采板1串口3"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}